## README
CBRE Powered Land - Design Studio: Engine Data Dictionary
Generated from source. Catalog version 1.
This workbook is every data point the design/engineering engine reads.
It is generated directly from the codebase (scripts/exportEquipmentWorkbook.ts),
so it always matches what the live tool computes. Re-run to refresh.
Sheet | Contents
Equipment - All | Every catalog item (racks, cooling, power) with full specs
Racks & AI Compute | GPU/AI racks and enterprise racks - chips, kW, weight, $, voltage
Cooling (MEP) | Chillers, dry coolers, CRAH, CDU, rear-door HX
Power (MEP) | Generators, UPS, switchgear, transformers, BESS, busway
Building Presets | Vendor archetypes (footprint, stories, cooling, PUE, rack mix)
Engine Parameters | Editable model parameters with defaults, units, and ranges
Cost Model | BOM unit rates ($/SF, $/MW, install factor, soft/contingency)
Efficiency Model | PUE base by cooling arch, climate adj, WUE/CUE bands
Grid Factors | EPA eGRID2023 carbon intensity by region (drives CUE/carbon)
Wet-Bulb | ASHRAE 0.4% design wet-bulb by metro (tower/WUE sizing)
Lead Times | Power-equipment procurement lead times
Engine Constants | Physical/calc constants (ton<->kW, rejection factor, slab psf)
Units convention | Dimensions in feet; power in kW at model layer (UI shows MW); cooling in tons.
Cost convention | indicativeUSD = facility hardware only. Silicon tracked separately as System $.
Confidence tags | high / med / low (specs); published / permit-derived / representative (presets).
Validation note | Values marked 'med'/'low' should be confirmed against the primary source before external publication.

## Equipment - All
ID | Category | Vendor class | Label | Capacity | Capacity unit | Cooling mode | Width (ft) | Depth (ft) | Height (ft) | Footprint (SF) | Weight (lb) | Facility hardware $ (BOM) | System $ incl. silicon | % heat to liquid | Input voltage | Output voltage | Availability | Lead time (wks) | Spec confidence | Source | Notes
rack-ent-air | Rack / AI compute | Enterprise 42U | Enterprise rack, air | 8 | kW | air | 2 | 3.9 | 7.2 | 7.8 | 1500 | 12000 | [8 empty] | Legacy air-cooled enterprise load.
rack-hd-rdhx | Rack / AI compute | High-density 48U | High-density rack, rear-door HX | 50 | kW | rdhx | 2 | 4.5 | 7.2 | 9 | 2000 | 28000 | [8 empty] | Passive/active rear-door heat exchanger.
rack-ai-nvl72 | Rack / AI compute | NVIDIA Blackwell GB200 NVL72 | NVIDIA GB200 NVL72 | 132 | kW | dlc | 2 | 4 | 7.2 | 8 | 3000 | 95000 | 3200000 | 0.87 | 415/480 AC 3ph | 54 VDC busbar | shipping |  | high | nvidia.com GB200 NVL72; SemiAnalysis; HPE QuickSpecs | Direct-to-chip liquid, CDU loop. ~2 L/s/rack, W32-W45.
rack-ai-nvl72-ultra | Rack / AI compute | NVIDIA Blackwell Ultra GB300 NVL72 | NVIDIA GB300 NVL72 | 142 | kW | dlc | 2 | 4 | 7.2 | 8 | 3300 | 110000 | 3850000 | 0.88 | 415/480 AC 3ph | 54 VDC busbar | shipping |  | high | nvidia.com; moduledge | Blackwell Ultra; DLC mandatory.
rack-gb200-nvl36 | Rack / AI compute | NVIDIA Blackwell GB200 NVL36 | NVIDIA GB200 NVL36 (single rack of pair) | 66 | kW | dlc | 2 | 4 | 7.2 | 8 | 1540 | 60000 | 1700000 | 0.87 | 415/480 AC 3ph | 54 VDC busbar | shipping |  | med | SemiAnalysis
rack-vr200-nvl72 | Rack / AI compute | NVIDIA Rubin (Oberon) | NVIDIA Vera Rubin VR200 NVL72 | 230 | kW | dlc | 2 | 4.3 | 7.5 | 8.6 | 4000 | 150000 | 8000000 | 0.92 | 800 VDC |  | roadmap |  | med | Ming-Chi Kuo (CES 2026); ModulEdge; SemiAnalysis | Max Q ~190 kW / Max P ~230 kW. Volume H2 2026. Flow ~2x GB300.
rack-kyber-nvl576 | Rack / AI compute | NVIDIA Rubin Ultra (Kyber) | NVIDIA Rubin Ultra Kyber NVL576 | 600 | kW | dlc | 2 | 4.3 | 7.5 | 8.6 |  | 200000 |  | 0.92 | 800 VDC |  | roadmap |  | low | NVIDIA GTC 2026; ModulEdge | H2 2027. Price not public.
rack-mi355x-dlc | Rack / AI compute | AMD CDNA4 (8-GPU node) | AMD Instinct MI355X node, DLC | 15 | kW | dlc | 2 | 4 | 1.4 | 8 |  | 45000 |  | 0.78 | 415/480 AC 3ph | 48 VDC | shipping |  | med | SemiAnalysis (AMD Advancing AI, Oct 2025) | NODE, not a rack-scale system. MI350X is the 1,000 W air sibling.
rack-helios-mi450x | Rack / AI compute | AMD CDNA5 (rack-scale) | AMD Helios MI400 / MI450X rack | 230 | kW | dlc | 2 | 4.3 | 7.5 | 8.6 |  | 150000 | 3000000 | 0.9 | 800 VDC |  | roadmap |  | low | hashrateindex; TechPowerUp | AMD's first rack-scale system. H2 2026.
chiller-1200 | Cooling - chiller | Centrifugal VFD | Centrifugal chiller, VFD | 1200 | ton |  | 24 | 7 | 8 | 168 |  | 1400000
chiller-1500 | Cooling - chiller | Centrifugal VFD | Centrifugal chiller, VFD | 1500 | ton |  | 26 | 8 | 8.5 | 208 |  | 1750000
drycooler-600 | Cooling - dry cooler | Adiabatic | Adiabatic dry cooler | 600 | ton |  | 24 | 12 | 9 | 288 |  | 320000
crah-100 | Cooling - CRAH | Hot-aisle CRAH | CRAH unit, hot-aisle | 100 | kW |  | 6 | 3.5 | 8 | 21 |  | 45000
cdu-l2l-1350 | Cooling - CDU | Liquid to liquid | CDU, liquid to liquid | 1350 | kW |  | 6 | 4 | 7.5 | 24 |  | 220000
cdu-l2l-2300 | Cooling - CDU | Liquid to liquid | CDU, liquid to liquid | 2300 | kW |  | 8 | 4.5 | 7.5 | 36 |  | 340000
cdu-l2a-70 | Cooling - CDU | Liquid to air, in-rack | CDU, liquid to air, in-rack | 70 | kW |  | 2 | 4 | 7.2 | 8 |  | 55000
rdhx-72 | Cooling - rear-door HX | Rear-door HX | Rear-door heat exchanger | 72 | kW |  | 2 | 1 | 7.2 | 2 |  | 18000
gen-2000 | Power - generator | Diesel Tier 4, 2 MW | Diesel genset, Tier 4, 2 MW class | 2000 | kW |  | 40 | 10 | 12 | 400 |  | 1100000 | [5 empty] | 78 | med | cmicglobal; powergenenterprises (2026) | Most >2 MW diesels ship EPA Tier 2; Tier 4 Final via SCR variant.
gen-4000 | Power - generator | Diesel Tier 4, 4 MW | Diesel genset, Tier 4, 4 MW class | 4000 | kW |  | 45 | 13 | 14 | 585 |  | 1900000 | [5 empty] | 78 | med |  | ~690 gCO2/kWh. Confirm tier per model (T2 vs T4F-SCR).
ups-5000 | Power - UPS | Static UPS, 5 MW block | UPS system, 5 MW block | 5000 | kW |  | 16 | 5 | 7.5 | 80 |  | 1250000 | [5 empty] | 32 | med | Wood Mackenzie T&D survey Q2 2025
swgr-mv | Power - switchgear | MV paralleling lineup | MV / paralleling switchgear lineup | 0 | kVA |  | 30 | 6 | 8 | 180 |  | 850000 | [5 empty] | 44 | high | Wood Mackenzie T&D survey Q2 2025
xfmr-3000 | Power - transformer | Liquid-filled | Transformer, 3 MVA | 3 | MVA |  | 8 | 6 | 8 | 48 |  | 220000 | [5 empty] | 90 | med | Wood Mackenzie T&D survey Q2 2025 | Substation power transformers run 128 wk, GSU 144 wk, large/custom 160+.
bess-2mwh | Power - BESS | LFP block | LFP BESS block | 2 | MWh |  | 30 | 8 | 9 | 240 |  | 600000
busway-800 | Power - busway | Overhead busway 800 A | Overhead busway, 800 A | 0 | kVA |  | 1 | 1 | 0.8 | 1 |  | 0 | [8 empty] | Cost rolled per linear foot in BOM; runlength-based.

## Racks & AI Compute
ID | Category | Vendor class | Label | Capacity | Capacity unit | Cooling mode | Width (ft) | Depth (ft) | Height (ft) | Footprint (SF) | Weight (lb) | Facility hardware $ (BOM) | System $ incl. silicon | % heat to liquid | Input voltage | Output voltage | Availability | Lead time (wks) | Spec confidence | Source | Notes
rack-ent-air | Rack / AI compute | Enterprise 42U | Enterprise rack, air | 8 | kW | air | 2 | 3.9 | 7.2 | 7.8 | 1500 | 12000 | [8 empty] | Legacy air-cooled enterprise load.
rack-hd-rdhx | Rack / AI compute | High-density 48U | High-density rack, rear-door HX | 50 | kW | rdhx | 2 | 4.5 | 7.2 | 9 | 2000 | 28000 | [8 empty] | Passive/active rear-door heat exchanger.
rack-ai-nvl72 | Rack / AI compute | NVIDIA Blackwell GB200 NVL72 | NVIDIA GB200 NVL72 | 132 | kW | dlc | 2 | 4 | 7.2 | 8 | 3000 | 95000 | 3200000 | 0.87 | 415/480 AC 3ph | 54 VDC busbar | shipping |  | high | nvidia.com GB200 NVL72; SemiAnalysis; HPE QuickSpecs | Direct-to-chip liquid, CDU loop. ~2 L/s/rack, W32-W45.
rack-ai-nvl72-ultra | Rack / AI compute | NVIDIA Blackwell Ultra GB300 NVL72 | NVIDIA GB300 NVL72 | 142 | kW | dlc | 2 | 4 | 7.2 | 8 | 3300 | 110000 | 3850000 | 0.88 | 415/480 AC 3ph | 54 VDC busbar | shipping |  | high | nvidia.com; moduledge | Blackwell Ultra; DLC mandatory.
rack-gb200-nvl36 | Rack / AI compute | NVIDIA Blackwell GB200 NVL36 | NVIDIA GB200 NVL36 (single rack of pair) | 66 | kW | dlc | 2 | 4 | 7.2 | 8 | 1540 | 60000 | 1700000 | 0.87 | 415/480 AC 3ph | 54 VDC busbar | shipping |  | med | SemiAnalysis
rack-vr200-nvl72 | Rack / AI compute | NVIDIA Rubin (Oberon) | NVIDIA Vera Rubin VR200 NVL72 | 230 | kW | dlc | 2 | 4.3 | 7.5 | 8.6 | 4000 | 150000 | 8000000 | 0.92 | 800 VDC |  | roadmap |  | med | Ming-Chi Kuo (CES 2026); ModulEdge; SemiAnalysis | Max Q ~190 kW / Max P ~230 kW. Volume H2 2026. Flow ~2x GB300.
rack-kyber-nvl576 | Rack / AI compute | NVIDIA Rubin Ultra (Kyber) | NVIDIA Rubin Ultra Kyber NVL576 | 600 | kW | dlc | 2 | 4.3 | 7.5 | 8.6 |  | 200000 |  | 0.92 | 800 VDC |  | roadmap |  | low | NVIDIA GTC 2026; ModulEdge | H2 2027. Price not public.
rack-mi355x-dlc | Rack / AI compute | AMD CDNA4 (8-GPU node) | AMD Instinct MI355X node, DLC | 15 | kW | dlc | 2 | 4 | 1.4 | 8 |  | 45000 |  | 0.78 | 415/480 AC 3ph | 48 VDC | shipping |  | med | SemiAnalysis (AMD Advancing AI, Oct 2025) | NODE, not a rack-scale system. MI350X is the 1,000 W air sibling.
rack-helios-mi450x | Rack / AI compute | AMD CDNA5 (rack-scale) | AMD Helios MI400 / MI450X rack | 230 | kW | dlc | 2 | 4.3 | 7.5 | 8.6 |  | 150000 | 3000000 | 0.9 | 800 VDC |  | roadmap |  | low | hashrateindex; TechPowerUp | AMD's first rack-scale system. H2 2026.

## Cooling (MEP)
ID | Category | Vendor class | Label | Capacity | Capacity unit | Cooling mode | Width (ft) | Depth (ft) | Height (ft) | Footprint (SF) | Weight (lb) | Facility hardware $ (BOM) | System $ incl. silicon | % heat to liquid | Input voltage | Output voltage | Availability | Lead time (wks) | Spec confidence | Source | Notes
chiller-1200 | Cooling - chiller | Centrifugal VFD | Centrifugal chiller, VFD | 1200 | ton |  | 24 | 7 | 8 | 168 |  | 1400000
chiller-1500 | Cooling - chiller | Centrifugal VFD | Centrifugal chiller, VFD | 1500 | ton |  | 26 | 8 | 8.5 | 208 |  | 1750000
drycooler-600 | Cooling - dry cooler | Adiabatic | Adiabatic dry cooler | 600 | ton |  | 24 | 12 | 9 | 288 |  | 320000
crah-100 | Cooling - CRAH | Hot-aisle CRAH | CRAH unit, hot-aisle | 100 | kW |  | 6 | 3.5 | 8 | 21 |  | 45000
cdu-l2l-1350 | Cooling - CDU | Liquid to liquid | CDU, liquid to liquid | 1350 | kW |  | 6 | 4 | 7.5 | 24 |  | 220000
cdu-l2l-2300 | Cooling - CDU | Liquid to liquid | CDU, liquid to liquid | 2300 | kW |  | 8 | 4.5 | 7.5 | 36 |  | 340000
cdu-l2a-70 | Cooling - CDU | Liquid to air, in-rack | CDU, liquid to air, in-rack | 70 | kW |  | 2 | 4 | 7.2 | 8 |  | 55000
rdhx-72 | Cooling - rear-door HX | Rear-door HX | Rear-door heat exchanger | 72 | kW |  | 2 | 1 | 7.2 | 2 |  | 18000

## Power (MEP)
ID | Category | Vendor class | Label | Capacity | Capacity unit | Cooling mode | Width (ft) | Depth (ft) | Height (ft) | Footprint (SF) | Weight (lb) | Facility hardware $ (BOM) | System $ incl. silicon | % heat to liquid | Input voltage | Output voltage | Availability | Lead time (wks) | Spec confidence | Source | Notes
gen-2000 | Power - generator | Diesel Tier 4, 2 MW | Diesel genset, Tier 4, 2 MW class | 2000 | kW |  | 40 | 10 | 12 | 400 |  | 1100000 | [5 empty] | 78 | med | cmicglobal; powergenenterprises (2026) | Most >2 MW diesels ship EPA Tier 2; Tier 4 Final via SCR variant.
gen-4000 | Power - generator | Diesel Tier 4, 4 MW | Diesel genset, Tier 4, 4 MW class | 4000 | kW |  | 45 | 13 | 14 | 585 |  | 1900000 | [5 empty] | 78 | med |  | ~690 gCO2/kWh. Confirm tier per model (T2 vs T4F-SCR).
ups-5000 | Power - UPS | Static UPS, 5 MW block | UPS system, 5 MW block | 5000 | kW |  | 16 | 5 | 7.5 | 80 |  | 1250000 | [5 empty] | 32 | med | Wood Mackenzie T&D survey Q2 2025
swgr-mv | Power - switchgear | MV paralleling lineup | MV / paralleling switchgear lineup | 0 | kVA |  | 30 | 6 | 8 | 180 |  | 850000 | [5 empty] | 44 | high | Wood Mackenzie T&D survey Q2 2025
xfmr-3000 | Power - transformer | Liquid-filled | Transformer, 3 MVA | 3 | MVA |  | 8 | 6 | 8 | 48 |  | 220000 | [5 empty] | 90 | med | Wood Mackenzie T&D survey Q2 2025 | Substation power transformers run 128 wk, GSU 144 wk, large/custom 160+.
bess-2mwh | Power - BESS | LFP block | LFP BESS block | 2 | MWh |  | 30 | 8 | 9 | 240 |  | 600000
busway-800 | Power - busway | Overhead busway 800 A | Overhead busway, 800 A | 0 | kVA |  | 1 | 1 | 0.8 | 1 |  | 0 | [8 empty] | Cost rolled per linear foot in BOM; runlength-based.

## Building Presets
ID | Vendor | Family | Era | Confidence | Length (ft) | Width (ft) | Stories | Clear height (ft) | Slab psf | Cooling arch | UPS redundancy | Gen redundancy | Target PUE | Target WUE | Rack rows | Total racks | IT load (MW) | Campus envelope (MW) | Summary
google-gen1-classic | google | Gen-1 Classic Single-Story | 2006-2012 | permit-derived | 450 | 230 | 1 | 30 | 250 | evaporative | 2N | N+1 | 1.12 | 1.1 | 20 | 1059 | 12 |  | Single-story warehouse, evaporative cooling towers, the original Google form.
google-gen2-doubledecker | google | Gen-2 Double-Decker | 2013-2015 | permit-derived | 330 | 250 | 2 | 32 | 300 | evaporative | 2N | N+1 | 1.11 | 1 | 40 | 2118 | 24 |  | Two-story greenfield, ~75-80 ft tall, evaporative cooling.
google-gen3-fourstory | google | Gen-3 Four-Story Vertical | 2016-2023 | permit-derived | 400 | 300 | 4 | 22 | 350 | evaporative | 2N | N+1 | 1.1 | 0.9 | 56 | 2480 | 50 |  | Four stories, data halls per floor, ML-optimized evaporative, max density per acre.
google-gen4-ai | google | Gen-4 AI Liquid-Cooled | 2024-present | published | 500 | 300 | 2 | 34 | 400 | evaporative | 2N | N+1 | 1.1 | 0.2 | 30 | 757 | 60.01 |  | Liquid-ready hybrid air + direct-to-chip, ~130 kW racks, TPU pods, gigawatt-campus context.
google-campus-gigawatt | google | Gigawatt Campus (composite) | 2024-present | permit-derived | 500 | 300 | 2 | 34 | 400 | evaporative | 2N | N+1 | 1.1 | 0.2 | 26 | 631 | 50.03 | 200 | Representative gigawatt campus: a Gen-4 lead building scaled, with campus power envelope.
Meta
AWS
Microsoft
Aligned
Vantage

## Engine Parameters
Group | Parameter | Unit | Default | Edited in
Building | Length (N-S) | ft | 400 | Parameters tab
Building | Width (E-W) | ft | 250 | Parameters tab
Building | Clear height | ft | 36 | Parameters tab
Building | Stories | count | 1 | Parameters tab
Building | Slab capacity | psf | 400 | Parameters tab
Building | Bay X | ft | 40 | Parameters tab
Building | Bay Y | ft | 40 | Parameters tab
Building | Column size | in | 24 | Parameters tab
Power | UPS redundancy | N / N+1 / 2N / 2N+1 | 2N | Parameters tab
Power | Gen redundancy | N / N+1 / 2N / 2N+1 | N+1 | Parameters tab
Power | Utility voltage | kV | 230 | model
Power | Service voltage | kV | 34.5 | model
Power | Fuel autonomy | hr | 48 | model
Cooling | Cooling architecture | evaporative/dlc/hybrid/... | hybrid | Parameters tab
Cooling | Cooling redundancy | N / N+1 / 2N / 2N+1 | N+1 | Parameters tab
Targets | Target PUE | ratio | 1.3 | Parameters tab
Targets | Target WUE | L/kWh | 0.3 | Parameters tab
Site | Climate | cold/temperate/hot | temperate | Parameters tab
Site | Grid region | eGRID subregion | US-avg | Parameters tab
Rack row | kW / rack | kW | (per catalog item) | Inspector
Rack row | Rack count | count | (per row) | Inspector
Rack row | Cooling mode | air/rdhx/dlc/immersion | (per catalog item) | Inspector
Rack row | Containment | hot/cold/none | hot | Inspector

## Cost Model
Item | Rate | Unit | Notes
Shell & structural (greenfield) | 55 | $/SF | Structural shell-and-core
Structural reinforcement (retrofit) | 22 | $/SF | Slab/roof reinforcement only
White-space fit-out | 180 | $/SF | Interior fit-out
Equipment install factor | 1.8 | x hardware | Labor, rigging, terminations
Electrical distribution | 2500000 | $/MW | MV/LV distribution, switchgear fit-out
Cooling distribution | 1500000 | $/MW | CW/CDU piping, pumps, glycol, headers
Fire protection | 150000 | $/MW | Detection + suppression (NFPA 855 for BESS)
BMS / DCIM controls | 250000 | $/MW
Commissioning | 200000 | $/MW | L1-L5 commissioning
Security | 100000 | $/MW | Access control, CCTV, perimeter
Civil / sitework | 500000 | $/MW | Grading, stormwater, roads
Right-of-way allowance | 2000000 | $ lump | Interconnect ROW
Zoning / entitlement allowance | 1500000 | $ lump
Overhead busway | 350 | $/linear ft
Soft costs | 0.095 | fraction | 9.5% of hard costs
Contingency | 0.1 | fraction | 10%

## Efficiency Model
Driver | Value | Notes
PUE base - evaporative | 1.1 | Evaporative + free-cooling + ML (hyperscale)
PUE base - immersion | 1.12
PUE base - dlc | 1.2 | Direct liquid cooling
PUE base - hybrid | 1.32
PUE base - chilled-water-air | 1.4
PUE base - air-only | 1.45 | Air heat rejection, near-zero water
Climate adj - cold | -0.03 | Added to base PUE
Climate adj - temperate | 0
Climate adj - hot | 0.04
Liquid floor | 1.06 | Best-case partial PUE a fully-liquid hall approaches
Liquid share weight | 0.55 | How far liquid load pulls estimate toward floor
WUE evaporative band (L/kWh) | 1.8-2.5 | NREL ref 0.7; dry-air 0
CUE definition | total CO2 (kg) / IT energy (kWh) = PUE x grid CO2 factor

## Grid Factors
Region | Label | CO2e (lb/MWh) | CO2e (kg/MWh) | Carbon-free %
SRVC | Northern Virginia (Ashburn) | 596.3 | 270.5 | 49.8
NWPP | Salt Lake City / NW Power Pool | 635.3 | 288.2 | 58.2
AZNM | Phoenix (AZ/NM) | 706.2 | 320.3 | 40.2
ERCT | Dallas (ERCOT) | 736.6 | 334.1 | 37.2
SRSO | Atlanta (SERC South) | 846 | 383.7 | 29.9
RFCW | Chicago / Columbus OH (RFC West) | 916.1 | 415.5 | 36
RMPA | Denver / Front Range | 1042.5 | 472.9 | 41.9
US-avg | National average fallback | 826.5 | 375 | 0
Source: EPA eGRID2023 Rev 2, Table 1 (CO2e, AR5)

## Wet-Bulb
Metro | Station | Design wet-bulb (F) | Confidence
Phoenix | KPHX | 76.1 | high
Northern Virginia | KIAD | 75 | med
Dallas-Fort Worth | KDFW | 78 | med
Chicago | KORD | 78 | med
Atlanta | KATL | 76.6 | med
Columbus OH | KCMH | 76.8 | med
Salt Lake City | KSLC | 66.3 | med
Source: ASHRAE Std 169 / Handbook of Fundamentals (0.4% evaporation WB)

## Lead Times
Item | Lead time (weeks) | Note
Substation power transformer (standard) | 128 | 160+ by mid-2026; custom to 208 (4 yr)
Generator step-up (GSU) transformer | 144
Pad-mount / unit-substation step-down | 78
Cast-resin dry transformer | 45
MV switchgear (paralleling) | 44
LV switchgear | 41
Diesel genset (2-3 MW) | 78
UPS (static, IGBT) | 32
Source: Wood Mackenzie T&D supply-chain survey, Q2 2025

## Engine Constants
Constant | Value | Unit | Notes
Ton to kW (thermal) | 3.517 | kW/ton | 12,000 BTU/hr
Heat rejection factor | 1.25 | x IT tons | Sheds chiller load + compressor heat
Air-cooling density limit | 30 | kW/rack | Above this, liquid is implied
Slab - standard floor | 250 | psf
Slab - AI/liquid default | 375 | psf | 350-400 recommended for AI
Slab - flag threshold | 300 | psf | Warn when AI/liquid and slab below
Hours per year | 8760 | hr | Annual energy/water/carbon
Liters per gallon | 3.7854 | L/gal
US avg grid CO2e | 0.375 | kg/kWh | Fallback when no region set
Solar land use | 6-8 | acres/MW_AC | NREL land-use analysis (Ong et al. + updates)
Facility load | IT kW x PUE | kW | Drives generation sizing