## README
Data Center 3D Component Catalog
Master dimension catalog for 3D-automating data center equipment (AI/GPU focus, whole facility). Compiled 2026-08-06.
How to use
Components tab | One row per equipment SKU. Width/Depth/Height in millimeters. Filter by Zone or Category. Add new rows following the Component_ID pattern (e.g. CMP-010).
Assemblies tab | How components combine (e.g. what's inside a GB200 NVL72 rack, an 8-rack pod). Use these as the parent-child structure for 3D scene assembly.
Standards_Reference tab | Exact spec constants (RU height, rail widths, PCIe card sizes, tile grid). These ARE millimeter-exact - build parametric rack/floor models from them.
Yellow cells | Your workflow columns: Verified_Date, 3D_Status, 3D_File_Path, LOD. Update as you verify dims and build models.
Axis & unit conventions
Width_mm (X) | Along the front face of the unit. For skids/yard equipment (gensets, chillers), X = the LONGEST plan dimension (noted per row).
Depth_mm (Y) | Front-to-back. For per-meter items (busway, cable tray), Depth = 1000 mm reference length or the standard section length (see Notes).
Height_mm (Z) | Vertical. Rack-mount gear: Height_mm should equal Height_RU x 44.45 (19in) or OU x 48 (OCP).
Rating_kW | Meaning given by Rating_Type: IT load (power draw), Cooling capacity, Heat rejection, or Electrical rating (throughput, kVA noted where applicable).
Dimension confidence - IMPORTANT
Current status | Web access was unavailable when this catalog was compiled, so no dimension could be checked against a live manufacturer datasheet. Nearly all rows are 'Estimated (recall)' - recalled from published datasheets, typically accurate within a few percent, but NOT yet millimeter-exact.
Workflow to mm-exact | 1) Open the Dim_Source page/datasheet. 2) Confirm W/D/H (and weight). 3) Change Dim_Confidence to 'Verified (datasheet)' and set Verified_Date. 4) Only model to final LOD from Verified rows. Standards_Reference values are already exact.
Confidence levels | Verified (datasheet) > Verified (standard) > Secondary (press/reseller) > Estimated (recall)
Catalog summary
Total components | 61
Verified rows | 1
Estimated rows | 60
Modeled (3D) | 0
Missing a dimension | 4
Suggested expansion order
Next items to add | GB300/Vera Rubin racks as specs publish; specific CDU models per vendor shortlist; fan walls; MV transformers per utility spec; security/DCIM gear; fire suppression (clean-agent tanks, VESDA); lighting; EPMS/BMS panels.

## Components
Component_ID | Zone | Category | Subcategory | Manufacturer | Model | Description | Width_mm | Depth_mm | Height_mm | Height_RU | Weight_kg | Rating_kW | Rating_Type | Mounting | Qty_Context | Dim_Source | Dim_Confidence | Verified_Date | 3D_Status | 3D_File_Path | LOD | Notes
RCK-001 | White Space | Rack | Enclosure | APC (Schneider) | NetShelter SX AR3100 | 42U server rack enclosure, 600W x 1070D | 600 | 1070 | 1991 | 42 | 131 |  |  | Floor-standing | Baseline enterprise rack | apc.com - AR3100 product page | Estimated (recall) |  | Not started |  | LOD100 Massing | Static load rating ~1364 kg
RCK-002 | White Space | Rack | Enclosure | APC (Schneider) | NetShelter SX AR3307 | 48U deep server rack enclosure, 600W x 1200D | 600 | 1200 | 2258 | 48 | 155 |  |  | Floor-standing | Deep rack for long servers | apc.com - AR3307 product page | Estimated (recall) |  | Not started |  | LOD100 Massing
RCK-003 | White Space | Rack | Enclosure | Vertiv | VR3357 | VR series 48U rack, 800W x 1200D | 800 | 1200 | 2265 | 48 |  |  |  | Floor-standing | Wide rack for cabling-heavy network rows | vertiv.com - VR rack family | Estimated (recall) |  | Not started |  | LOD100 Massing | 800 mm width eases cable management
RCK-004 | White Space | Rack | AI Rack System | NVIDIA | GB200 NVL72 | Rack-scale system: 18x 1U compute trays + 9x NVSwitch trays, liquid-cooled MGX/ORv3-derived rack | 600 | 1068 | 2236 |  | 1360 | 120 | IT load | Floor-standing | 1 per NVL72 system | nvidia.com/en-us/data-center/gb200-nvl72 | Estimated (recall) |  | Not started |  | LOD100 Massing | ~120 kW rack; ~1360 kg widely cited by NVIDIA; verify vs NVIDIA MGX/OCP contribution
RCK-005 | White Space | Rack | AI Rack System | NVIDIA | GB300 NVL72 | Next-gen NVL72 rack (Blackwell Ultra); same rack envelope class as GB200 NVL72 | 600 | 1068 | 2236 |  |  | 135 | IT load | Floor-standing | 1 per NVL72 system | nvidia.com - GB300 NVL72 page | Estimated (recall) |  | Not started |  | LOD100 Massing | Envelope assumed = GB200 NVL72; power ~135-140 kW - verify
RCK-006 | White Space | Rack | Open Rack Spec | Open Compute Project | Open Rack v3 (ORv3) | ORv3 base rack; 21 in (538 mm) equipment bay; 48 mm OU pitch | 600 | 1068 | 2300 |  |  |  |  | Floor-standing | Spec reference for OCP/MGX gear | opencompute.org - Open Rack specs | Estimated (recall) |  | Not started |  | LOD100 Massing | 538 mm bay + 48 mm OU are spec constants; overall H/D vary by config
CMP-001 | Rack IT Gear | Compute | GPU Server | NVIDIA | DGX H100 | 8U appliance, 8x H100 SXM5 + 2x Xeon 8480C | 482.2 | 897.1 | 356 | 8 | 130.45 | 10.2 | IT load | 19in rack-mount | Up to 4 per rack (air-cooled) | nvidia.com - DGX H100 datasheet | Estimated (recall) |  | Not started |  | LOD100 Massing | Datasheet recall: 19.0 x 35.3 x 14.0 in; 287.6 lb
CMP-002 | Rack IT Gear | Compute | GPU Server | NVIDIA | DGX H200 | 8U appliance, 8x H200 SXM (same chassis as DGX H100) | 482.2 | 897.1 | 356 | 8 | 130.45 | 10.2 | IT load | 19in rack-mount | Up to 4 per rack (air-cooled) | nvidia.com - DGX H200 datasheet | Estimated (recall) |  | Not started |  | LOD100 Massing | Same chassis as DGX H100 per NVIDIA
CMP-003 | Rack IT Gear | Compute | GPU Server | NVIDIA | DGX B200 | 10U appliance, 8x B200 SXM | 482.2 | 897.1 | 444 | 10 | 142 | 14.3 | IT load | 19in rack-mount | 2-3 per rack typical | nvidia.com - DGX B200 datasheet | Estimated (recall) |  | Not started |  | LOD100 Massing | ~17.5 in H; ~313 lb; ~14.3 kW max
CMP-004 | Rack IT Gear | Compute | GPU Compute Tray | NVIDIA | GB200 NVL72 compute tray | 1U liquid-cooled MGX tray, 2x GB200 superchips (2 Grace + 4 Blackwell) | 538 |  | 44.5 | 1 OU |  | 5.4 | IT load | 21in OCP rack-mount | 18 per NVL72 rack | nvidia.com - GB200 NVL72 | Estimated (recall) |  | Not started |  | LOD100 Massing | Width = ORv3 bay; depth/weight not published; ~5.4 kW/tray inferred
CMP-005 | Rack IT Gear | Compute | NVSwitch Tray | NVIDIA | GB200 NVL72 NVSwitch tray | 1U liquid-cooled NVLink switch tray (2x NVSwitch ASICs) | 538 |  | 44.5 | 1 OU |  |  |  | 21in OCP rack-mount | 9 per NVL72 rack | nvidia.com - GB200 NVL72 | Estimated (recall) |  | Not started |  | LOD100 Massing | Depth/weight/power not published
CMP-006 | Rack IT Gear | Compute | GPU Server | Supermicro | SYS-821GE-TNHR | 8U GPU SuperServer, HGX H100 8-GPU | 447 | 833 | 356 | 8 |  | 10.2 | IT load | 19in rack-mount | Up to 4 per rack (air-cooled) | supermicro.com - SYS-821GE-TNHR | Estimated (recall) |  | Not started |  | LOD100 Massing | 17.6 x 32.8 x 14 in recall
CMP-007 | Rack IT Gear | Compute | GPU Server | Dell | PowerEdge XE9680 | 6U server, HGX H100/H200 8-GPU | 482 | 1009 | 263.2 | 6 | 105 | 10.2 | IT load | 19in rack-mount | Up to 4 per rack | dell.com - PowerEdge XE9680 spec sheet | Estimated (recall) |  | Not started |  | LOD100 Massing | Weight/power approx (6x 2800 W PSU config)
CMP-008 | Rack IT Gear | Compute | Server | Dell | PowerEdge R760 | Mainstream 2U 2-socket rack server | 482 | 772 | 86.8 | 2 | 34 | 1 | IT load | 19in rack-mount | ~20 per rack | dell.com - PowerEdge R760 spec sheet | Estimated (recall) |  | Not started |  | LOD100 Massing | Depth config-dependent (~740-772 mm)
CMP-009 | Rack IT Gear | Compute | Server | Dell | PowerEdge R660 | Mainstream 1U 2-socket rack server | 482 | 749 | 42.8 | 1 | 21 | 0.7 | IT load | 19in rack-mount | ~40 per rack | dell.com - PowerEdge R660 spec sheet | Estimated (recall) |  | Not started |  | LOD100 Massing
GPU-001 | Rack IT Gear | GPU Module | PCIe Accelerator | NVIDIA | H100 PCIe 80GB | Dual-slot full-height full-length PCIe Gen5 accelerator | 38 | 268 | 111 |  |  | 0.35 | IT load | PCIe slot | Up to 8 per PCIe server | nvidia.com - H100 product page | Estimated (recall) |  | Not started |  | LOD100 Massing | W=thickness (2 slots), D=length 10.5 in, H=bracket height; 300-350 W TDP
STO-001 | Rack IT Gear | Storage | All-Flash Node | Dell | PowerScale F710 | 1U all-flash NVMe scale-out NAS node (R660-based) | 482 | 749 | 42.8 | 1 | 22 | 0.8 | IT load | 19in rack-mount | Clusters of 3+ | dell.com - PowerScale F710 spec sheet | Estimated (recall) |  | Not started |  | LOD100 Massing | Chassis dims inferred from R660 base platform
NET-001 | Rack IT Gear | Networking | InfiniBand Switch | NVIDIA | Quantum-2 QM9700 | 1U 64-port NDR 400G InfiniBand switch (32x OSFP) | 438 | 660 | 44 | 1 | 17 | 1.7 | IT load | 19in rack-mount | Leaf/spine fabric | nvidia.com - QM9700 datasheet | Estimated (recall) |  | Not started |  | LOD100 Massing | Power = max with active cables; ~0.75 kW passive
NET-002 | Rack IT Gear | Networking | Ethernet Switch | NVIDIA | Spectrum-4 SN5600 | 2U 64-port 800GbE switch (OSFP) | 438 |  | 88 | 2 |  |  |  | 19in rack-mount | AI Ethernet fabric | nvidia.com - SN5600 datasheet | Estimated (recall) |  | Not started |  | LOD100 Massing | Depth/weight/power to verify
NET-003 | Rack IT Gear | Networking | Ethernet Switch | NVIDIA | Spectrum-3 SN4700 | 1U 32-port 400GbE switch (QSFP-DD) | 438 | 550 | 44 | 1 | 11.5 | 0.45 | IT load | 19in rack-mount | Spine/leaf | nvidia.com - SN4700 datasheet | Estimated (recall) |  | Not started |  | LOD100 Massing
NET-004 | Rack IT Gear | Networking | ToR Switch | Arista | 7050SX3-48YC8 | 1U 48x25G + 8x100G ToR switch | 439 | 441 | 44 | 1 | 9.5 | 0.19 | IT load | 19in rack-mount | 1-2 per rack | arista.com - 7050X3 datasheet | Estimated (recall) |  | Not started |  | LOD100 Massing | Typical draw; max ~0.36 kW
RPW-001 | Rack IT Gear | Rack Power | Vertical PDU | APC (Schneider) | AP8841 | Metered rack PDU 2G, ZeroU, 200-208 V 30 A, 36 outlets | 56 | 76 | 1829 | 0U | 8 | 5 | Electrical rating | 0U vertical | 2 per rack (A+B feeds) | apc.com - AP8841 product page | Estimated (recall) |  | Not started |  | LOD100 Massing | 5.0 kW = 24 A derated at 208 V
RPW-002 | Rack IT Gear | Rack Power | Power Shelf | OCP (Delta/LiteOn) | ORv3 33 kW power shelf | 33 kW ORv3 power shelf (6x 5.5 kW PSUs, 48 Vdc busbar) | 538 |  | 44.5 | 1 OU |  | 33 | Electrical rating | 21in OCP rack-mount | 8 per GB200 NVL72 rack | opencompute.org - Open Rack project | Estimated (recall) |  | Not started |  | LOD100 Massing | Depth/weight vary by design
LCL-001 | White Space | Liquid Cooling | In-rack CDU | CoolIT Systems | CHx200 | 4U rack-mount liquid-to-liquid CDU for DLC | 442 | 813 | 178 | 4 | 68 | 200 | Cooling capacity | 19in rack-mount | 1 per DLC rack (in-rack option) | coolitsystems.com - CHx200 | Estimated (recall) |  | Not started |  | LOD100 Massing | ~200 kW at low approach temp; dry weight
LCL-002 | White Space | Liquid Cooling | Row CDU | Vertiv | Liebert XDU 1350 | Floor-standing row-level liquid-to-liquid CDU | 750 | 1200 | 2000 |  | 950 | 1350 | Cooling capacity | Floor-standing | 1 per 6-10 DLC racks | vertiv.com - Liebert XDU family | Estimated (recall) |  | Not started |  | LOD100 Massing | Rack-form footprint, sits in row
LCL-003 | White Space | Liquid Cooling | Rear-door HX | Motivair | ChilledDoor | Active rear-door heat exchanger replacing rack rear door | 600 | 305 | 1999 |  | 150 | 75 | Cooling capacity | Rack rear door | 1 per rack | motivaircorp.com - ChilledDoor | Estimated (recall) |  | Not started |  | LOD100 Massing | Height shown for 42U rack; 48U ~2265 mm
LCL-004 | White Space | Liquid Cooling | Liquid-to-air sidecar | CoolIT Systems | AHx240 | Liquid-to-air sidecar heat exchanger for DLC racks (NVL72 class) | 600 | 1200 | 2265 |  | 400 | 240 | Cooling capacity | Floor-standing | 1 sidecar per 1-2 racks | coolitsystems.com - AHx240 | Estimated (recall) |  | Not started |  | LOD100 Massing | Rejects DLC heat to room air; no facility water needed
ACL-001 | White Space | Air Cooling | In-row cooler | Vertiv | Liebert CRV CR040RA | 600 mm wide chilled-water in-row cooling unit | 600 | 1100 | 1996 |  | 390 | 40 | Cooling capacity | Floor-standing | 1 per 4-6 air-cooled racks | vertiv.com - Liebert CRV | Estimated (recall) |  | Not started |  | LOD100 Massing | ~40 kW sensible; 300 mm DX variants exist
ACL-002 | White Space | Air Cooling | Perimeter CRAH | Vertiv | Liebert CW146 | Large-frame downflow chilled-water CRAH | 2921 | 889 | 1969 |  | 1250 | 146 | Cooling capacity | Floor-standing | Perimeter of hall | vertiv.com - Liebert CW | Estimated (recall) |  | Not started |  | LOD100 Massing | CW family 26-232 kW; downflow into raised-floor plenum
PDW-001 | White Space | Power Distribution | Overhead busway | Starline | T5 Series 800 A | Overhead track busway, continuous-access slot (cross-section per m run) | 146 | 1000 | 171 |  | 16 | 554 | Electrical rating | Overhead suspended | 2 runs per row (A+B) | starlinepower.com - T5 busway | Estimated (recall) |  | Not started |  | LOD100 Massing | W x H cross-section; Depth col = 1 m ref length; ~16 kg/m; 3 m sections
PDW-002 | White Space | Power Distribution | Floor PDU | Vertiv | Liebert FPC 225 kVA | Floor PDU cabinet with isolation transformer + panelboards | 1372 | 914 | 1930 |  | 1590 | 225 | Electrical rating | Floor-standing | End of row | vertiv.com - Liebert FPC | Estimated (recall) |  | Not started |  | LOD100 Massing | Rating 225 kVA; smaller frames narrower
PDW-003 | White Space | Power Distribution | Remote power panel | Eaton | RPP 400 A | Remote power panel, up to 4 panelboards | 610 | 305 | 2134 |  | 270 |  |  | Floor-standing | In-row / end of row | eaton.com - RPP | Estimated (recall) |  | Not started |  | LOD100 Massing | 24 x 12 x 84 in typical; no transformer
STR-001 | White Space | Structure | Raised floor panel | Tate | ConCore 1000 | Concrete-core steel raised access floor panel, 24 x 24 in | 609.6 | 609.6 | 28.6 |  | 18 |  |  | Floor tile | Full hall grid | tateinc.com - ConCore | Estimated (recall) |  | Not started |  | LOD100 Massing | Metric markets use 600 x 600 mm; pedestal FFH typ 300-1200 mm
CPW-001 | White Space | Cable Pathway | Wire basket tray | Legrand Cablofil | CF54/300 | Welded steel wire-mesh cable tray (cross-section per m) | 300 | 1000 | 54 |  | 1.4 |  |  | Overhead suspended | Per cable run | legrand.us - Cablofil | Estimated (recall) |  | Not started |  | LOD100 Massing | 54 mm depth x 300 mm width; 3 m sections; ~1.4 kg/m
CPW-002 | White Space | Cable Pathway | Fiber raceway | Panduit | FiberRunner FR4X4 | 4 x 4 in fiber routing channel with hinged cover (per section) | 101.6 | 1829 | 101.6 |  |  |  |  | Overhead suspended | Per fiber run | panduit.com - FiberRunner | Estimated (recall) |  | Not started |  | LOD100 Massing | 6 ft sections; fittings keep 2 in bend radius
CPW-003 | White Space | Cable Pathway | Fiber raceway | Panduit | FiberRunner FR12X4.5 | 12 x 4.5 in high-capacity fiber channel (per section) | 304.8 | 1829 | 114.3 |  |  |  |  | Overhead suspended | Trunk fiber routes | panduit.com - FiberRunner | Estimated (recall) |  | Not started |  | LOD100 Massing | Also 6x4 and 24x4 sizes
CPW-004 | White Space | Cable Pathway | Ladder rack | Chatsworth (CPI) | Universal Cable Runway 12in | Tubular steel ladder rack (per 10 ft section) | 305 | 3048 | 38 |  | 12.5 |  |  | Overhead suspended | Copper/power routes | chatsworth.com - Cable Runway | Estimated (recall) |  | Not started |  | LOD100 Massing | 229 mm rung spacing
CPW-005 | White Space | Cable Pathway | Ladder rack | Chatsworth (CPI) | Universal Cable Runway 18in | Tubular steel ladder rack (per 10 ft section) | 457 | 3048 | 38 |  | 15 |  |  | Overhead suspended | Copper/power routes | chatsworth.com - Cable Runway | Estimated (recall) |  | Not started |  | LOD100 Massing | Widths 152-914 mm in family
CNT-001 | White Space | Containment | Aisle end door | Chatsworth (CPI) | Aisle Containment Sliding Door | Dual sliding end-of-aisle containment door | 1219 | 100 | 2438 |  |  |  |  | Floor-standing | 2 per contained aisle | chatsworth.com - Aisle Containment | Estimated (recall) |  | Not started |  | LOD100 Massing | Fits nominal 1200 mm aisle; roof panels ~600 x 1200 mm; Depth = frame thickness est.
ELC-001 | Gray Space | Electrical | UPS - large 3-phase | Vertiv | Liebert EXL S1 1200 kVA | Monolithic transformer-free UPS, 1200 kVA/kW lineup | 3300 | 991 | 2134 |  | 4990 | 1200 | Electrical rating | Floor-standing | N+1 lineups per hall | vertiv.com - EXL S1 (datasheet SL-25999) | Estimated (recall) |  | Not started |  | LOD100 Massing | Excludes battery cabinets; tolerance ~10%
ELC-002 | Gray Space | Electrical | UPS - large 3-phase | Schneider Electric | Galaxy VX 1500 kVA | Modular-scalable large UPS lineup | 5600 | 970 | 1970 |  | 5500 | 1500 | Electrical rating | Floor-standing | N+1 lineups per hall | se.com - Galaxy VX | Estimated (recall) |  | Not started |  | LOD100 Massing | Lineup width varies ~4.5-6.5 m with I/O + bypass cabinets
ELC-003 | Gray Space | Electrical | UPS - modular | Vertiv | Liebert APM2 600 kW | Modular UPS frame, 30-600 kW hot-swap modules | 1200 | 900 | 2000 |  | 1600 | 600 | Electrical rating | Floor-standing | Scalable blocks | vertiv.com - APM2 | Estimated (recall) |  | Not started |  | LOD100 Massing | ~700 kg empty, ~1600 kg populated
ELC-004 | Gray Space | Electrical | UPS - modular | Eaton | 93PM 200 kW frame | Modular 3-phase UPS, up to 200 kW per cabinet | 862 | 926 | 1876 |  | 820 | 200 | Electrical rating | Floor-standing | Scalable blocks | eaton.com - 93PM | Estimated (recall) |  | Not started |  | LOD100 Massing | Larger frames 1240-2100 mm wide
ELC-005 | Gray Space | Electrical | Battery cabinet | Vertiv | HPL Li-ion battery cabinet | Lithium-ion battery cabinet for large UPS | 700 | 855 | 2065 |  | 1230 |  |  | Floor-standing | Multiple per UPS lineup | vertiv.com - HPL | Estimated (recall) |  | Not started |  | LOD100 Massing | ~60-130 kWh per cabinet; weight varies with module count
ELC-006 | Gray Space | Electrical | LV switchgear | Eaton | Magnum DS (per section) | LV 480/600 V metal-enclosed drawout switchgear, one vertical section | 813 | 1524 | 2286 |  | 1360 |  |  | Floor-standing | Multi-section lineups | eaton.com - Magnum DS | Estimated (recall) |  | Not started |  | LOD100 Massing | Section widths 559/660/813 mm; depths 1372-1829 mm
ELC-007 | Gray Space | Electrical | MV switchgear | Eaton | VacClad-W 15 kV (per section) | MV 15 kV metal-clad vacuum switchgear, one vertical section | 914 | 2388 | 2413 |  | 2720 |  |  | Floor-standing | Multi-section lineups | eaton.com - VacClad-W | Estimated (recall) |  | Not started |  | LOD100 Massing | 36 x 94 x 95 in typical, two-high breakers
ELC-008 | Gray Space | Electrical | Transformer | ABB (generic) | 2500 kVA dry-type cast-resin | Unit-substation cast-resin transformer in enclosure | 2500 | 1500 | 2450 |  | 6300 | 2500 | Electrical rating | Pad-mounted | 1 per unit substation | Manufacturer datasheet (vendor-specific) | Estimated (recall) |  | Not started |  | LOD100 Massing | Rating in kVA; dims vary ~15% by BIL/vendor
ELC-009 | Gray Space | Electrical | Static transfer switch | Vertiv | Liebert STS2 1000 A | Static transfer switch, 2-source, 1000 A 480 V | 1638 | 840 | 1981 |  | 1090 |  |  | Floor-standing | Per dual-feed PDU group | vertiv.com - STS2 | Estimated (recall) |  | Not started |  | LOD100 Massing | 250-600 A frames ~813-1200 mm wide
ELC-010 | Gray Space | Electrical | ATS | ASCO | 7000 Series 3000 A | Automatic transfer switch, 3000 A 480 V, floor enclosure | 1969 | 1219 | 2286 |  | 1500 |  |  | Floor-standing | Per generator feed | ascopower.com - 7000 Series | Estimated (recall) |  | Not started |  | LOD100 Massing | Bypass-isolation option adds ~50-80% width
BKP-001 | Yard | Backup Power | Diesel genset (open) | Caterpillar | 3516B (2000 kW standby) | Diesel genset, open skid, 2000 kW / 2500 kVA | 6100 | 2170 | 2620 |  | 15500 | 2000 | Electrical rating | Skid | N+1 per campus block | cat.com - 3516B spec sheet | Estimated (recall) |  | Not started |  | LOD100 Massing | W col = skid length, D col = skid width; dry weight; radiator-cooled
BKP-002 | Yard | Backup Power | Diesel genset (open) | Cummins | QSK95 (3500 kW) | Diesel genset, open skid, 3.5 MW standby | 6800 | 2440 | 2900 |  | 26000 | 3500 | Electrical rating | Skid | N+1 per campus block | cummins.com - DQL spec sheet | Estimated (recall) |  | Not started |  | LOD100 Massing | W col = length
BKP-003 | Yard | Backup Power | Enclosed genset | Cat/Cummins (generic) | 3 MW in 40 ft-class enclosure | Genset in weatherproof sound-attenuated enclosure with sub-base tank | 12192 | 2438 | 3960 |  | 45000 | 3000 | Electrical rating | Pad-mounted | Yard rows | Vendor enclosure drawings | Estimated (recall) |  | Not started |  | LOD100 Massing | 40 ft footprint; height 2.9-4.5 m with attenuators; weight excl fuel
MEC-001 | Yard | Mechanical Plant | Air-cooled chiller | Carrier | 30XA-1002 | Air-cooled screw chiller, ~1000 kW (285 ton) | 11937 | 2253 | 2297 |  | 9600 | 1000 | Cooling capacity | Rooftop/Yard | Chiller yard rows | carrier.com - 30XA | Estimated (recall) |  | Not started |  | LOD100 Massing | W col = length; operating weight
MEC-002 | Yard | Mechanical Plant | Air-cooled chiller | Vertiv | Liebert AFC (1 MW) | Air-cooled freecooling screw chiller | 10750 | 2250 | 2540 |  | 10000 | 1000 | Cooling capacity | Rooftop/Yard | Chiller yard rows | vertiv.com - Liebert AFC | Estimated (recall) |  | Not started |  | LOD100 Massing | Range 500-1700 kW; length 7-13.5 m
MEC-003 | Gray Space | Mechanical Plant | Water-cooled chiller | York (JCI) | YK centrifugal (~1500 ton) | Water-cooled centrifugal chiller, ~5275 kW | 4880 | 2240 | 2740 |  | 15900 | 5275 | Cooling capacity | Floor-standing | Central plant | johnsoncontrols.com - YK | Estimated (recall) |  | Not started |  | LOD100 Massing | W col = length; dims vary with shell codes
MEC-004 | Yard | Mechanical Plant | Cooling tower | BAC | Series 3000 (12x18 ft cell) | Induced-draft crossflow cooling tower, single cell | 5486 | 3658 | 4900 |  | 18000 | 4000 | Heat rejection | Rooftop/Yard | Multi-cell banks | baltimoreaircoil.com - Series 3000 | Estimated (recall) |  | Not started |  | LOD100 Massing | Operating weight; ~900-1150 nominal tons/cell
MEC-005 | Yard | Mechanical Plant | Dry cooler | Guntner | GFD V-shape (1 MW) | V-coil dry cooler with EC fans | 12000 | 2275 | 2850 |  | 7000 | 1000 | Heat rejection | Rooftop/Yard | Rows along yard | guntner.com - GFD | Estimated (recall) |  | Not started |  | LOD100 Massing | W col = length; scales ~2.9 m per fan pair
MEC-006 | Gray Space | Mechanical Plant | Pump skid | Bell & Gossett | e-1510 base-mounted (100 HP) | End-suction centrifugal CHW pump + motor on baseplate | 2030 | 910 | 1220 |  | 900 | 75 | Electrical rating | Skid | Central plant | xylem.com - e-1510 | Estimated (recall) |  | Not started |  | LOD100 Massing | W col = base length; varies by pump/motor size
MEC-007 | Yard | Mechanical Plant | Thermal storage | DN Tanks / CB&I | Chilled water TES ~1 MG | Site-built stratified CHW TES tank, ~3800 m3 | 15240 | 15240 | 21336 |  |  |  |  | Pad-mounted | Optional per plant | Project-specific drawings | Estimated (recall) |  | Not started |  | LOD100 Massing | Cylindrical: W/D = diameter; project-specific example
FUE-001 | Yard | Fuel | Storage tank | Generic (UL-2085) | 20,000 gal protected AST | Double-wall fire-protected diesel storage tank | 10973 | 3048 | 3400 |  | 29500 |  |  | Pad-mounted | Per genset group | Vendor drawing (Fireguard type) | Estimated (recall) |  | Not started |  | LOD100 Massing | 10 ft dia x 36 ft shell; empty weight; height incl saddles
REF-001 | Reference | Reference | ISO container | ISO 668 | 40 ft (1AA) container | Standard 40 ft ISO container external envelope | 12192 | 2438 | 2591 |  | 3750 |  |  | Pad-mounted | Containerized equipment ref | ISO 668 standard | Verified (standard) |  | Not started |  | LOD100 Massing | ISO 668 exact values; high-cube 2896 mm; tare ~3700-3900 kg

## Assemblies
Assembly_ID | Assembly_Name | Component_ID | Component | Qty | Placement_Notes
ASM-001 | NVIDIA GB200 NVL72 rack | RCK-004 | Rack frame (MGX/ORv3-derived, liquid-cooled) | 1 | Overall envelope ~600 x 1068 x 2236 mm; blind-mate liquid manifolds at rear
ASM-001 | NVIDIA GB200 NVL72 rack | CMP-004 | GB200 compute tray (1U MGX) | 18 | Stacked in two banks; 9 above and 9 below the NVSwitch section (typical layout)
ASM-001 | NVIDIA GB200 NVL72 rack | CMP-005 | NVSwitch tray (1U) | 9 | Center of rack; NVLink cable cartridge / blind-mate backplane connects trays
ASM-001 | NVIDIA GB200 NVL72 rack | RPW-002 | ORv3 33 kW power shelf | 8 | Top and/or bottom of rack; feeds 48 Vdc busbar; total ~132 kW capacity for ~120 kW load
ASM-002 | Example DLC AI pod (8-rack row) | RCK-004 | GB200 NVL72 rack | 8 | Single row, 600 mm rack pitch; hot aisle at rear
ASM-002 | Example DLC AI pod (8-rack row) | LCL-002 | Row CDU (Liebert XDU class) | 2 | Ends of row; N+1 coolant distribution to rack manifolds
ASM-002 | Example DLC AI pod (8-rack row) | PDW-001 | Overhead busway run (A+B) | 2 | Two runs above the row; plug-in units drop to each rack
ASM-002 | Example DLC AI pod (8-rack row) | CNT-001 | Aisle end door | 2 | Hot-aisle containment; roof panels span rack tops
ASM-002 | Example DLC AI pod (8-rack row) | NET-001 | QM9700 fabric switch | 4 | In network racks at row end (not counted here); scale-out fabric

## Standards_Reference
Standard | Parameter | Value_mm | Value_note | Notes
Unit conversion | 1 inch | 25.4 | exact | All imperial datasheet values convert at exactly 25.4 mm/in
EIA-310 (19in rack) | 1 rack unit (RU/U) height | 44.45 | exact | 1.75 in; stack RU x 44.45 for mounted equipment heights
EIA-310 (19in rack) | Panel/faceplate width | 482.6 | exact | The '19 inches'
EIA-310 (19in rack) | Rail opening (usable width) | 450.85 | exact | 17.75 in between rails
EIA-310 (19in rack) | Mounting hole horizontal spacing | 465.1 | exact | 18.312 in center-to-center
EIA-310 (19in rack) | Hole pattern within 1U |  | 15.875 / 15.875 / 12.7 | Repeating vertical hole spacing pattern per U
OCP Open Rack v3 | 1 OpenU (OU) height | 48 | exact | OCP rack unit pitch
OCP Open Rack v3 | Equipment bay width | 538 | exact | The '21 inch' bay; GB200 NVL72 trays use this
OCP Open Rack v3 | Typical rack external width | 600 | nominal | Same footprint width class as EIA racks
PCIe CEM spec | Full-height card height | 111.15 | exact | 4.376 in
PCIe CEM spec | Low-profile card height | 68.9 | exact
PCIe CEM spec | Full-length card length | 312 | exact | 12.283 in
PCIe CEM spec | Half-length card length | 167.65 | exact
PCIe CEM spec | Slot pitch (single slot) | 20.32 | exact | 0.8 in; dual-slot card occupies ~2 pitches
Raised floor (US) | Standard tile | 609.6 | 609.6 x 609.6 | 24 x 24 in; metric markets 600 x 600 mm
Raised floor | Typical finished floor height |  | 300 - 1200 | 150-1800 mm available; set by airflow/pipe needs
Layout convention | Cold aisle width (typical) | 1219.2 | 2 tiles | 48 in typical minimum for equipment install
Layout convention | Hot aisle width (typical) | 914.4 | 1.5 tiles | 36 in typical minimum
Layout convention | Row pitch (7-tile hot/cold layout) | 4267.2 | 7 tiles | Common repeating pitch: rack depth + both aisles
ISO 668 | 40 ft container L x W x H |  | 12192 x 2438 x 2591 | Exact; high-cube height 2896 mm